## flammability_chart
Ternary Plot Instructions
Enter data in columns A-E (Yellow)
Gray and green shaded cells are calculated | [8 empty] | CORNER LABELS | [5 empty] | REFERENCE LINES
Enter corner labels in table to the right | [8 empty] | O2 | 0 | 0 |  |  |  | Triangle | 0 | 0
[9 empty] | Fuel | 50 | 100 |  |  |  | Triangle | 50 | 100
[9 empty] | N2 | 100 | 0 |  |  |  | Triangle | 100 | 0
[15 empty] | Triangle | 0 | 0
[15 empty] | 1 | 20 | 0
[5 empty] | CALCULATED | [9 empty] | 1 | 60 | 80
ENTER DATA HERE | [5 empty] | Raw Data |  |  |  | Transformed Data |  |  |  |  | 2 | 40 | 0
Zone | Sample ID | Raw Data |  |  |  | Normalized to 100 |  |  |  | X | Y |  |  |  | 2 | 70 | 60
|  | Top | Left | Right | SUM | TOP | LEFT | RIGHT | SUM | =RIGHT+(TOP/2) | =TOP |  |  |  | 3 | 60 | 0
Upper | A |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | 3 | 80 | 40
Upper | B |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | 4 | 80 | 0
Upper | C |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | 4 | 90 | 20
Upper | D |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | 5 | 20 | 0
Lower | E |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | 5 | 10 | 20
Lower | F |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | 6 | 40 | 0
Lower | G |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | 6 | 20 | 40
Lower | H |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Note: X-Y axes are scaled from -10 to 110 |  |  | 7 | 60 | 0
[15 empty] | 7 | 30 | 60
[13 empty] | Cst(%) | 75 | 8 | 80 | 0
[13 empty] | LFL in O2 | 3 | 8 | 40 | 80
[13 empty] | UFL in O2 | 80 | 9 | 10 | 20
[13 empty] | MOC | 8.1 | 9 | 90 | 20
[15 empty] | 10 | 20 | 40
[15 empty] | 10 | 80 | 40
[15 empty] | 11 | 30 | 60
[15 empty] | 11 | 70 | 60
[15 empty] | 12 | 40 | 80
[15 empty] | 12 | 60 | 80
[15 empty] | airLine | 79 | 0
[15 empty] | airLine | 50 | 100
[15 empty] | LFL in air | 78.217 | 2.7
[15 empty] | UFL in air | 68.56 | 36
[15 empty] | Cst | 12.5 | 25
[15 empty] | Cst Line | 12.5 | 25
[15 empty] | Cst Line | 100 | 0
[15 empty] | LFL in O2 | 1.5 | 3
[15 empty] | UFL in O2 | 40 | 80
[15 empty] | MOC | 95.95 | 1.1571
Enter Corner
Labels Here

## ISO10156 Method
| H2 [vol%] | CO2 [vol%] | Ki | N2 equivalent of CO2[vol%] | Normalized hydrogen concentration [vol%] | Inference |  |  |  |  | For multiple diluent
| 7 | bal | 1.5 | 139.5 | 4.7782 | since Tci for H2 (5.7) > 4.77, the mixture is non flammable |  |  |  |  | Gas | vol% | N2 equivalent | % diluent | 1/MXCmixture | MXCmixture[%]
[11 empty] | CH4 | 16.4 | - | 16.4 | 8.7735 | 11.3979
[11 empty] | N2 | 25.08 | 25.08 | 30
[11 empty] | CO2 | 58.52 | 87.78 | 70
Since the diluent is present(11.39) less than fuel concentration(16.4), the mixture is non-flammable
Ki | Nitrogen equivalency
Gas | N2 | CO2 | He | Ar | Ne | Kr | Xe | SO2 | SF6 | CF4
Ki | 1 | 1.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1.5 | 1.5 | 1.5 | For multiple fuel
Gas | H2 | CO | Methane | Ethane | Butanes | Ethylene | Propane | Propene’s | Acetylene | n-Hexane | Gas | vol%
Tci | 5.7 | 20 | 8.7 | 7.6 | 5.7 | 6 | 6 | 6.5 | 4 | 3.5 | CH4 | 1.12 | 81.94% | 94.4% | Since the below inequality satishfied, the mixture is flammable
[11 empty] | C3H8 | 4.48
Tci is the maximum concentration of that gas that is "safe" in nitrogen. | [10 empty] | N2 | 94.4
the amount of inerting gas you need to stop a fire
the amount of inerting gas available in the mixture
| (100/Tci)-1 | Dilution Factor
at what concentration that mixture becomes flammable when it leaks into the air.
Can be use for - Set LEL Detectors -Ventilation Design -Safe Handling of Fuel-Inert Blends

## Venti_LEL
LEL Detectors Limit set | [7 empty] | Ventilation Design
|  | Tci | inert fraction | Ki | 1/MXCmixture | MXCmixture | 20% LEL Alarm | MXCmixture | industry practice to stay below
CH4 | 90% | 8.7 |  |  | 95.4483 | 1.048% | 0.2095% | 1.048% | 25%
N2 | 10% |  | 0.11111 | 1 |  |  |  | ventilation must ensure the concentration of the leaked gas blend never exceeds of the compartment volume
in lab we use 50% LEL CH4 cylinder to calibrate 20% LEL 100% CH4 LEL = 5% by volume, so we use 2.5 vol% CH4. H2 100% LEL=4 vol%, 20% LEL=0.8 vol% H2 | [8 empty] | 0.2619%
[8 empty] | The gas leak rate | target safe concentration (as a decimal) | The Mixing Factor | The resulting required air flow
[8 empty] | G (SCCM) | Climit (20% LEL of H2) | k | Qair (SCCM) | Qair (lit/min) | Qair (m3/h)
[8 empty] | 500 | 0.008 | 3 | 187500 | 187.5 | 11.25
calibration factor |  | 2.5
Calibrating your LEL detector with the "50-for-20" rule (using Methane to mimic a heavy hydrocarbon) significantly changes how it perceives Hydrogen (H2). In a laboratory environment focused on high-pressure gas safety and H2 handling, this cross-calibration acts as a massive "sensitivity booster." | [7 empty] | Air Changes per Hour (ACH) |  | Enclosure size(m3)
[8 empty] | 0.1125 |  | 100
[8 empty] | needs | 8.8889 | hours to change the air in the full enclosure
Industry Standard Benchmarks for ACH
In standard LEL sensors, Hydrogen typically has a Response Factor (RF) of approximately 0.8 to 0.9 relative to Methane. This means H2 is actually "easier" for the sensor to detect than Methane. If a sensor is calibrated 1:1 for Methane, it will already naturally over-read H2. | [8 empty] | Standard Laboratory | 4-8 ACH
[9 empty] | Chemical Storage/Process Areas | 8-12 ACH
[9 empty] | High-Hazard/Fume Hood Areas | 12-15+ ACH
Displayed % LEL
H2 leak vol% | H2 LEL% | Calibration factor | response factor | The sensor will read |  |  |  | The "Pocket" Hazard: Although 187 LPM of fresh air technically dilutes a 0.5 lit/min leak to safe levels globally, H2 is extremely buoyant. In a 100 m3 enclosure, H2 will not distribute evenly; it will rise and collect in "pockets" at the highest points (e.g., between ceiling joists or above light fixtures).
1.3 | 6.5% | 2.5 | 0.8 | 20.31%
Extreme Early Warning. Because the sensor is "tuned up" to find heavy naphtha/toluene fractions, it becomes hyper-sensitive to H2. It will go into a 20% LEL alarm when the actual hydrogen concentration is only about 1.2% or 1.3% LEL. This is an excellent "fail-safe" for high-pressure H2 testing. The detector will no longer give you a scientifically accurate "True LEL" for H2. It will always over-report the danger. In a safety context, this is usually acceptable, but it can lead to "nuisance alarms" where the system shuts down even though the H2 levels are still technically well below the explosive limit.
G (Leak Rate)
k = Mixing Factor
[6 empty] | Climit (Safety Target) |  | k = 1: Perfect, instantaneous mixing (rarely happens). k = 2 to 3: Good mixing (active mechanical ventilation). k = 5 to 10: Poor mixing (natural ventilation or stagnant corners). Check the area of your enclosure. Assuming 100 m3, then 4 vol% H2(100%LEL) means 4 m3 H2 and 96 m3 Air inside the enclosure which is explosive. then decide the dilution you need to make it non explosive and calculate ventilation rate.
[5 empty] | Q air | The Steady-State Dilution
Since you deal with hydrogen embrittlement and high-pressure boosters, detecting a leak at the earliest possible physical moment is more important than knowing the exact concentration.
purge time
To calculate the ventilation rate required for a 100 m3 enclosure during a detector failure, we must ensure the steady-state concentration of Hydrogen never reaches the Lower Explosive Limit (LEL).
Leak rate | 1 | L/h | 16.6667 | SCCM
H2 LEL[100%] | 4 | vol%
20% LEL | 0.8 | vol%
Q air | 10416.6667 | SCCM | 10.4167 | LPM | 0.010417 | m3/min
Volume of enclosure | 100 | m3
Air Changes per Hour | 0.00625 | ACH | enclosure needs 160 hours to change the air in the enclosure just once
160
Cinitial | 0.8
Cfinal | 0.04 | standard industrial practice
t(purge time) | 479.3172 | h
t(purge time) | 29.9573 | min, if ACH = 6

## LFL
propane in a mixture of 21 % oxygen + 79 % Nitrogen, air
The LFL is sensitive to pressure, so this calculation assumes atmospheric pressure.
Assumptions | ΔHc (propane) | 2024 | kJ/mol
limiting adiabatic flame temperature of 1600 K | Tad,limit | 1600 | K
the energy released by the combustion of the fuel is exactly equal to the energy required to raise the temperature of the entire mixture (fuel + air) from the initial state to the threshold flame temperature | T0 | 298 | K
| Cp,avg | 31.5 | J/mol/K | averaged between 298 K & 1600 K |  |  | P in | Mpa
| ΔT | 1302 | K
| Qreq | 41.013 | kJ/mol | Heat Required per mole of mixture |  |  | at P= | 30 | bar | 3 | Mpa
For a fuel-lean mixture (which defines the LFL), the mole fraction of propane is very small. Therefore, we can assume the heat capacity of the total mixture is approximately equal to the heat capacity of air. | LFL | 2.0263 | vol%
[7 empty] | LFLp | 1.8426 | vol%
propane in a mixture of 21 % oxygen + 79 % CO2
65.61%
Carbon dioxide is a triatomic molecule with more vibrational modes than diatomic nitrogen. Its average heat capacity between 298 K and 1600K is approximately 52 J/mol/K
| Cp,avg for O2 | 33 | J/mol/K |  | The LFL is higher in a CO2 mixture because CO2 has a higher molar heat capacity. Thermal Ballast: To reach the required 1600 K for a self-sustaining flame, the combustion of propane must provide enough energy to heat up all the surrounding inert molecules. Since each molecule of CO2 can absorb more energy per degree of temperature rise than N2, you need to burn more propane (increase the concentration) to generate enough total heat to reach that threshold. This is why using CO2 for inerting your high-pressure boosters or reactor systems is more efficient than using N2; you need roughly 66% less gas to achieve the same level of fire suppression.
(Limiting Adiabatic Flame Temperature): The minimum temperature a flame must reach to provide enough kinetic energy for the combustion reaction to remain self-sustaining. For many hydrocarbons in air, this is roughly 1500–1600 K | Cp,avg for CO2 | 52 | J/mol/K
| Mixture Cp,avg | 48.01 | J/mol/K
| Qreq | 62.509 | kJ/mol
| LFL | 3.0884 | vol%
Combustion is a chemical reaction, and like all reactions, its speed depends on temperature according to the Arrhenius Equation:k=Ae^(-Ea/RT); As the fuel concentration drops (moving toward the LFL), the flame temperature also drops. When the temperature falls toward 1600 K, the reaction rate decreases exponentially. Above 1600 K: The reaction is fast enough to release heat faster than it is lost to the environment. The flame is "stable." If a mixture cannot even theoretically reach 1600 K under adiabatic (no heat loss) conditions, it is physically impossible for it to sustain a flame in the real world where heat losses are always present.